| 697 CPCB II 115 KW ENGINE SPECIFICATIONS |  |  |
| --- | --- | --- |
| ENGINE CATEGORY(Domestic/Imported) |  | Domestic |
| GENSET CATEGORY(Constant Speed/Variable Speed) |  | Constant Speed |
| NAME AND ADDRESS OF THE ENGINE MANUFACTURER (Type Approval Certificate Owner) |  | M/s TATA MOTORS LIMITED. |
| ADDRESS OF THE MANUFACTURING PLANT/S |  | Pune |
| 1 | ENGINE |  |
| 1.1 | Engine Type | Compression Ignition, Direct Injection |
| 1.2 | Engine Layout (INLINE/V) | INLINE |
| 1.3 | Type of Aspiration | Turbocharged & Intercooled |
| 1.4 | Working principle (Four-Stroke/Two-Stroke) | Four-Stroke |
| 1.5 | Emission Compliant | CPCB-II |
| 1.6 | Bore (mm) | 97 |
| 1.7 | Stroke (mm) | 128 |
| 1.8 | Number of Cylinders | 6 |
| 1.9 | Firing Order | 1-5-3-6-2-4 |
| 1.10 | Engine Displacement (l) | 5.7 |
| 1.11 | Type of fuel used | Diesel |
| 1.12 | Gross Rated Power (kW) | 115 |
| 1.13 | Rated Speed (RPM) | 1500 |
| 1.14 | Frequency (Hz) | 50 |
| 1.15 | Max No Load Speed (rpm) | 1590 ±15 |
| 1.16 | Piston Speed (m/s) | 6.4 |
| 1.17 | Over load Capability | No Overloading |
| 1.18 | Compression Ratio (With Tolerance) | 17.5 : 1 |
| 1.19 | Type of combustion chamber (Hemispherical / squish/others) | Re-Entrant Toroidal Type |
| 1.20 | Max. Dry Weight kg | 500 kg appx |
| 1.21 | Max. Wet Weight kg | 520 kg appx |
| 2 | COOLING SYSTEM |  |
| 2.1 | Type | Liquid cooled |
| 2.2 | Nature of liquid and proportion | Water : Coolant (50:50) |
| 2.3 | Circulating pump yes/no | Yes |
| 2.4 | Circulating pump type | Centrifugal |
| 2.5 | Drive ratio | 1.34 : 1 |
| 2.6 | Thermostat type and setting | SOT 88°C ± 2°C |
| 2.7 | Minimum CAP Pressure (Psi) | 7 |
| 2.8 | Max. Top tank temperature | 100° C |
| 3 | LUBRICATING SYSTEM |  |
| 3.1 | Type of lubrication | Forced Lubrication |
| 3.2 | Minimum oil pressure | 1 |
| 3.3 | Minimum Oil pressure | 8 |
| 3.4 | Maximum Oil temperature | 125° C |
| 3.5 | Oil sump capacity low | 12 |
| 3.6 | Oil sump capacity high | 14 |
| 3.7 | Total system oil capacity | 15.5 |
| 3.8 | Lubricating oil grade | SAE 15W40 CI4 + |
| 4 | AIR INTAKE SYSTEM |  |
| 4.1 | Air filter type | Dry Type |
| 5 | FUEL SYSTEM |  |
| 5.1 | Type of injection System | Mechanical Inline |
| 5.2 | Make | Bosch India Ltd |
| 5.3 | Injection timing deg BTDC (specify tolerance) | 09 deg ± 1 BTDC |
| 5.4 | Governor |  |
| A | Type | Bosch Mechanical- RSV type |
| 6 | ELECTRICALS |  |
| 6.1 | Starter Motor Type/Voltage | Positive engagement /12 V |
| 6.2 | Charging Alternator Specifications | 12 V |
| 7 | COLD START |  |
| 7.1 | Cold start capability | Min. 5° C to be assessed through trials |